## Function
Parameter | Helper | Error value | escalated | error code
A0 | 0 | 1 | 1 | 1
A1 | 1 | 8 | 4 | 9
A2 | 2 | 2 | 2 | 12
A3 | 3 | 2 | 2 | 17
A4 | 4 | 2 | 2 | 22
A5 | 5 | 8 | 4 | 29
B0 | 6 | 1 | 1 | 31
B1 | 7 | 8 | 4 | 39
B2 | 8 | 2 | 2 | 42
B3 | 9 | 2 | 2 | 47
B4 | 10 | 2 | 2 | 52
B5 | 11 | 8 | 4 | 59
B6 | 12 | 8 | 4 | 64
B7 | 13 | 8 | 4 | 69
C0 | 14 | 8 | 4 | 74
C1 | 15 | 8 | 4 | 79
C2 | 16 | 8 | 4 | 84
C3 | 17 | 8 | 4 | 89
C4 | 18 | 8 | 4 | 94
C5 | 19 | 8 | 4 | 99
C6 | 20 | 8 | 4 | 104
C7 | 21 | 8 | 4 | 109
W0 | 22 | 8 | 4 | 114
W1 | 23 | 8 | 4 | 119
W2 | 24 | 8 | 4 | 124
W3 | 25 | 0 | 0 | 125

## Sheet2
Char | Value | Alarm | Device Error Code
A0 | 0 | No Alarm | 0
A0 | 1 | Ambient Temp. Sensor Alarm | 1
A0 | 2 | High Control Temperature Alarm | 2
A0 | 4 | PT7 High Temperature Alarm | 3
A0 | 8 | Low Control Temperature Alarm | 4
A1 | 0 | No Alarm | 5
A1 | 1 | Supply Temp Sensor Alarm (Latched) | 6
A1 | 2 | External RTD Sensor Alarm | 7
A1 | 4 | Return Temperature Sensor Alarm | 8
A1 | 8 | External Thermistor Sensor Alarm | 9
A2 | 0 | No Alarm | 10
A2 | 1 | Low Coolant Level Alarm (Latched) | 11
A2 | 2 | Low Process Flow Alarm | 12
A2 | 4 | Low Plant Flow Alarm | 13
A2 | 8 | Current Sensor 1 Alarm | 14
A3 | 0 | No Alarm | 15
A3 | 1 | PT7 Low Temperature Alarm | 16
A3 | 2 | High Ambient Temperature Alarm | 17
A3 | 4 | Low Ambient Temperature Alarm | 18
A3 | 8 | External Connector Not Installed | 19
A4 | 0 | No Alarm | 20
A4 | 1 | Default High Temperature Alarm | 21
A4 | 2 | Default Low Temperature Alarm | 22
A4 | 4 | No Process Flow Alarm | 23
A4 | 8 | Fan Failure Alarm | 24
A5 | 0 | No Alarm | 25
A5 | 1 | Current Sensor 2 Alarm | 26
A5 | 2 | Internal 2.5V Reference Alarm | 27
A5 | 4 | Internal 5V Reference Alarm | 28
A5 | 8 | System Error Alarm (Global) | 29
B0 | 0 | No Alarm | 30
B0 | 1 | Reserved (Not Used) | 31
B0 | 2 | Reserved (Not Used) | 32
B0 | 4 | Reserved (Not Used) | 33
B0 | 8 | Reserved (Not Used) | 34
B1 | 0 | No Alarm | 35
B1 | 1 | ADC System Error Alarm | 36
B1 | 2 | I2C System Error Alarm | 37
B1 | 4 | EEPROM System Error Alarm | 38
B1 | 8 | Watchdog System Error Alarm | 39
B2 | 0 | No Alarm | 40
B2 | 1 | Reserved (Not Used) | 41
B2 | 2 | Reserved (Not Used) | 42
B2 | 4 | Reserved (Not Used) | 43
B2 | 8 | Reserved (Not Used) | 44
B3 | 0 | No Alarm | 45
B3 | 1 | ADC Reset Error Alarm | 46
B3 | 2 | ADC Calibration Error Alarm | 47
B3 | 4 | ADC Conversion Error Alarm | 48
B3 | 8 | Reserved (Not Used) | 49
B4 | 0 | No Alarm | 50
B4 | 1 | IO Expender Acknowledge Error Alarm | 51
B4 | 2 | PSA IO Expender Acknowoledge Alarm | 52
B4 | 4 | RTC Acknowledge Error Alarm | 53
B4 | 8 | Reserved (Not Used) | 54
B5 | 0 | No Alarm | 55
B5 | 1 | I2C SCL Low Error Alarm | 56
B5 | 2 | I2C SDA Low Error Alarm | 57
B5 | 4 | EEPROM 1 (U201) Acknowledge Alarm | 58
B5 | 8 | EEPROM 2 (U200) Acknowledge Alarm | 59
B6 | 0 | No Alarm | 60
B6 | 1 | Reserved (Not Used) | 61
B6 | 2 | Reserved (Not Used) | 62
B6 | 4 | Reserved (Not Used) | 63
B6 | 8 | Reserved (Not Used) | 64
B7 | 0 | No Alarm | 65
B7 | 1 | EEPROM 1 (U201) Read Error Alarm | 66
B7 | 2 | EEPROM 1 (U201) Write Error Alarm | 67
B7 | 4 | EEPROM 2 (U200) Read Error Alarm | 68
B7 | 8 | EEPROM 2 (U200) Write Error Alarm | 69
C0 | 0 | No Alarm | 70
C0 | 1 | External RTD Sensor Open Alarm | 71
C0 | 2 | External RTD Sensor Short Alarm | 72
C0 | 4 | Return Temp Sensor Open Alarm | 73
C0 | 8 | Return Temp Sensor Open Alarm | 74
C1 | 0 | No Alarm | 75
C1 | 1 | Global Supply Temp Sensor Alarm | 76
C1 | 2 | Supply Temp Sensor Locked Alarm | 77
C1 | 4 | Supply Temp Sensor Open Alarm | 78
C1 | 8 | Supply Temp Sensor Short Alarm | 79
C2 | 0 | No Alarm | 80
C2 | 1 | Internal 2.5V Reference High Alarm | 81
C2 | 2 | Internal 2.5V Reference Low Alarm | 82
C2 | 4 | Internal 5V Reference High Alarm | 83
C2 | 8 | Internal 5V Reference Low Alarm | 84
C3 | 0 | No Alarm | 85
C3 | 1 | External Therm. Sensor Open Alarm | 86
C3 | 2 | External Therm. Sensor Short Alarm | 87
C3 | 4 | Ambient Temp Sensor Open Alarm | 88
C3 | 8 | Ambient Temp Sensor Short Alarm | 89
C4 | 0 | No Alarm | 90
C4 | 1 | Reserved (Not Used) | 91
C4 | 2 | Reserved (Not Used) | 92
C4 | 4 | Reserved (Not Used) | 93
C4 | 8 | Reserved (Not Used) | 94
C5 | 0 | No Alarm | 95
C5 | 1 | Current Sensor 1 Open Alarm | 96
C5 | 2 | Current Sensor 1 Short Alarm | 97
C5 | 4 | Current Sensor 2 Open Alarm | 98
C5 | 8 | Current Sensor 2 Short Alarm | 99
C6 | 0 | No Alarm | 100
C6 | 1 | Rear Left Fan Noise Alarm | 101
C6 | 2 | Rear Right Fan Noise Alarm | 102
C6 | 4 | Front Left Fan Noise Alarm | 103
C6 | 8 | Front Right Fan Noise Alarm | 104
C7 | 0 | No Alarm | 105
C7 | 1 | Rear Left Fan Open Alarm | 106
C7 | 2 | Rear Right Fan Open Alarm | 107
C7 | 4 | Front Left Fan Open Alarm | 108
C7 | 8 | Front Right Fan Open Alarm | 109
W0 | 0 | No Alarm | 110
W0 | 1 | Low Process Flow Warning | 111
W0 | 2 | Process Fluid Level Warning | 112
W0 | 4 | Switch to Supply Temp as Control Temp Warning | 113
W0 | 8 | Reserved (Not Used) | 114
W1 | 0 | No Alarm | 115
W1 | 1 | High Control Temp Warning | 116
W1 | 2 | Low Control Temp Warning | 117
W1 | 4 | High Ambient Temp Warning | 118
W1 | 8 | Low Ambient Temp Warning | 119
W2 | 0 | No Alarm | 120
W2 | 1 | Reserved (Not Used) | 121
W2 | 2 | Reserved (Not Used) | 122
W2 | 4 | Reserved (Not Used) | 123
W2 | 8 | Reserved (Not Used) | 124
W3 | 0 | No Alarm | 125
W3 | 1 | Reserved (Not Used) | 126
W3 | 2 | Reserved (Not Used) | 127
W3 | 4 | Reserved (Not Used) | 128
W3 | 8 | Reserved (Not Used) | 129